╓───────────────────────────────────┐

██║                                   │

██║               FAULT               │

██║         SHAREWARE MANUAL          │

██║                            v. 1.0 │

██╚═══════════════════════════════════╛

▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀▀

Written by

Kevin Sitton

Rolla, MO 65401

i.   Introduction

Thank you for looking at FAULT Three Phase Fault

Analysis.  It is a three phase fault calculation

program written for the Texas Instruments TI-85

calculator.  It uses the point-to-point computation

method to estimate fault current levels at defined

buses.

ii.  System Requirements

■ TI-85 graphing calculator

■ Graph-Link 85 computer link

■ IBM PC (or compatible), or MacIntosh computer.  (computer

specification details outlined in link documentation)

iii. Disclaimer

■	This program is designed for quick on-site field

calculations.  The TI-85 is perfect to pull out of your

pocket and run a fast fault comparison from two

different contribution locations, or to determine if

you have enough of an interrupting capacity with your

overcurrent protective devices.  However, this program

uses the point-to-point method to calculate potential

fault currents.  It is not intended to take the place

of comprehensive fault calculation software packages,

which use more sophisticated calculation techniques and

more extensive libraries.

■	Nothing in the software was written or intended to be a

virus or any other destructive program.  Not re-sponsible for damage, lost files, or any other problem

resulting from use or misuse of the program in altered

or unaltered form.

MENUS & SELECTIONS

I.   "FAULT" Menu

The main menu gives the user four choices.  They

are "Circuit Elements," "Execute Analysis", "View

Result" and "EXIT" on function keys F1, F2, F3 and F5

respectively.  Pressing F1 brings up the "Circuit

Elements" menu, which allows the user to choose the

type of element between two buses.  F2 will execute the

fault current calculation for the buses just entered.

F3 will store the bus output current values to an

output list and allow the user to view them.  F5 will

terminate the program.

II.  "Circuit Elements" Menu

The "Circuit Elements" menu gives the user four

choices.  They are "Contributions," "Feeders" and

"Transformers."  F1 allows the user to input the

beginning available short circuit current contribution

from the service utility.  F2 inserts a feeder run

between buses.  F3 inserts a transformer.  F5 will take

the user back to the main menu.

III. "Contributions"

The user has a choice of single or three phase,

and short circuit current contribution form, being

either in units of AMPS, or in KVA.  This contribution

value is where the calculation begins.  The user MUST

start with this value.  The bus number is the number

the user gives to the bus where the contribution enters

the power distribution system.

IV.  "Feeders"

The feeder is the cable run between two (2) buses.

The user is prompted for single or three phase, cable

details, such as size, length of run, number of cables

per phase, etc.  The user is also asked for the type of

conduit; which is either magnetic (steel), or non-

magnetic (PVC, air, etc.).  Feeder sizes are restricted

to the values listed in table 1.

--menus & selections cont.

V.   "Transformers"

The transformer is placed between two (2) buses.

The user is prompted for single or three phase and

transformer details, such as primary and secondary

voltages, size in KVA, and percent impedance (%Z).

Where possible, use name-plate info.  Other generic

values are listed in Table 2.

EXAMPLE SYSTEM

I.		You must start with a fault contribution.  From

"Circuit Elements," choose "Contributions."  Begin from

the utility connection.  The UTILITY in the sample

system is listed as having 68,950 amps available at

4,160 volts.  It is three phase, and in units of amps.

Enter the correct values when prompted for them.  BE

SURE OF YOUR INPUT VALUES.  This version of the program

does not use an editor, so you can not go back and

change the numbers after you have entered them.  If you

make a mistake, you must restart the program.

II.		The feeder from the utility connection to the main

service transformer is one 100ft run of 750MCM aluminum

cable per phase.  It is three phase. It is in air so

the conduit is non-magnetic.  The cable is configured

as three separate cables; not multi-conductor cable.

The other feeders in the example are entered in a

similar fashion.

IV.		The main service transformer is a 2000KVA 4160/480

three phase device.  Its percent impedance (%Z) is

given as name-plate information.

V.		Feeder voltages and transformer primary voltages

are taken from their corresponding upstream element

values automatically.  Therefore, contribution voltage

values and transformer secondary voltages MUST be

entered correctly.  Buses must start with "1"  and must

be consecutive; you cannot skip a number.  For example,

1-2, 2-3, 2-4, 3-5, etc. is acceptable, but 1-2, 2-4,

10-11, etc. is not.  Keeping your inputs concise and

not jumping around will speed the calculations.

***NOTE***

A good field use for this program is to compare the fault levels for a

feeder run as supplied by one panel against a panel in a different location on

the site.  This would be accomplished by analyzing 2 contribution points at

once.   From contribution point 1 (bus 1) to fault point 1 (bus 2), and from

contribution point 2 (bus 3) to fault point 1 (bus 4).  Notice that the 2

systems are separate, but the buses are numbered consecutively.

SAMPLE SYSTEM DIAGRAM

1-750MCM Aluminum/PHASE      8-500MCM Copper/PHASE       4-500MCM Cu/PHASE

in air from                 in 8-3" PVC              in 4-3"PVC 50 ft

╔═══════1╗ substn.↓ ╔2═══════3╗           ↓   10 ft.   ╔═════4════╗↓ ╔═5══╗

║UTILITY ╠═════════>╣ 2000KVA ╠═══════════════════════>╣          ╠═>╣ MTR╟

║ 69,850 ║  100 ft. ║TRANSFOR.║  1-#2 Cu/ϕ↓ 1"PVC 5'   ║   MAIN   ║  ║ CTL╟

║  AMPS  ║          ║4160/480 ║    ╔═══════════════════╣   DIST.  ║  ║ CTR╟

║ AVAIL. ║          ║  5.0%Z  ║    ║       2-250MCM Cu ║   PANEL  ║  ╚════╝

║ 4160V  ║          ║   3/ϕ   ║    ║       PER ϕ  ╔════╣          ║  ╔════╗

║  3/ϕ   ║          ╚═════════╝    ║        2"PVC ↓ 75'║    3/ϕ   ╠═>╣PLNT║

╚════════╝                         ↓            ╔═╩7═╗ ╚══════════╝  ║HVAC║

╔══╩═════8╗     ║OFFC║              ↑╚═6══╝

║  75KVA  ║     ║HVAC║        2-250MCM Cu/PHASE

╔════11╗                ║TRANSFOR.║     ╚════╝          in 2-2"PVC  75'

╢      ║                ║ 480/208 ║  1-#2 Copper ╔13═══════╗

╢OFFICE║    1-#6 Copper ║  1.6%Z  ║   1"PVC  5'  ║         ║

╢ LTG. ╠←════════╗ ←    ║   3/ϕ   ║       ╔═════>╣  LTG.   ║

╢PANEL ║         ║3/4"  ╚═════9╦══╝       ║      ║  DIST.  ║

╢ 1/ϕ  ║         ║  PVC        ║ 2-1/0 Cu ║      ║  PANEL  ║  ╔14══╗

╚══════╝         ║             ║← per ϕ   ║      ║         ║  ║OTD.╟

║  10'        ↓  1.5"PVC ║      ║   1/ϕ   ║  ║LTG.╟

║          ╔══╩10═╗ 82'  ║      ╚══╦═══╦══╝╔>╣PNL.╟

╔════12╗         ╚══════════╣OFFICE║      ║         ║   ║   ║ ║    ╟

║      ║    1-#6 Copper     ║POWER ╠══════╝         ║   ╚═══╝ ╚════╝

║COMPS.╠←═══════╗←3/4"PVC   ║DIST. ║                ║     ↑   ╔15══╗

║  &   ║        ╚═══════════╣PANEL ║               >╚════════>╣IN- ╟

║ UPS  ║           25'      ║ 3/ϕ  ║             1-#6 Copper  ║DOOR╟

║ 1/ϕ  ║                    ╚══════╝               3/4" PVC   ║LTG.╟

╚══════╝                                              50'     ║PNL.╟

╚════╝

BUS SCC VALUES

╔═══════════════════════════════════╗

║  BUS 1=69850A      BUS 8=38617A   ║

║                                   ║

║  BUS 2=61618A      BUS 9=11354A   ║

║                                   ║

║  BUS 3=44136A      BUS 10=7944A   ║

║                                   ║

║  BUS 4=43762A      BUS 11=6037A   ║

║                                   ║

║  BUS 5=40341A      BUS 12=4438A   ║

║                                   ║

║  BUS 6=32515A      BUS 13=7463A   ║

║                                   ║

║  BUS 7=32515A      BUS 14=3004A   ║

║                                   ║

║            BUS 15=3004A           ║

╚═══════════════════════════════════╝

TABLES

Table 1                  Table 2

╒═══════╤═══════╤═══════╤═══════╕  ╒═══════════╕

│  KVA  │  %Z(Ω)│  %R(Ω)│  %X(Ω)│  │Feeder Size│

╞═══════╪═══════╪═══════╪═══════╡  ╞═════╤═════╡

│   3.0 │ 3.8907│ 3.7600│ 1.0000│  │   14│  3/0│

│   6.0 │ 3.2182│ 2.7200│ 1.7200│  │   12│  4/0│

│   9.0 │ 2.5849│ 2.3100│ 1.1600│  │   10│  250│

│  15.0 │ 2.7789│ 2.1000│ 1.8200│  │    8│  300│

│  30.0 │ 1.6000│ 0.8876│ 1.3312│  │    6│  350│

│  45.0 │ 1.7000│ 0.9429│ 1.4145│  │    4│  400│

│  75.0 │ 1.6000│ 0.8876│ 1.3312│  │    3│  500│

│ 112.5 │ 1.0000│ 0.5547│ 0.8321│  │    2│  600│

│ 150.0 │ 1.2000│ 0.6657│ 0.9985│  │    1│  750│

│ 225.0 │ 1.2000│ 0.6657│ 0.9985│  │  1/0│ 1000│

│ 300.0 │ 1.2000│ 0.6657│ 0.9985│  │  2/0│ XXXX│

│ 500.0 │ 1.3000│ 0.7211│ 1.0816│

─────┴─────┘

│ 750.0 │ 3.5000│ 0.6317│ 3.4425│

│1000.0 │ 3.5000│ 0.6048│ 3.4474│

│1500.0 │ 3.5000│ 0.5617│ 3.4546│

│2000.0 │ 5.0000│ 0.7457│ 4.9441│

│2500.0 │ 5.0000│ 0.7457│ 4.9441│

───────┴───────┴───────┴───────┘

This is the first version of the FAULT program.  It will

probably have a few bugs and/or problems.  I am throwing it out

to the public and will be awaiting comment.  (either for or

against)  If there is enough interest, I will try to write an

editor for it, because just like everyone else, I get really

irritated when I have to abort the program if I make a mistake.

So....PLEEEAAASE.... let me know what you think.

Kevin Sitton

161 Woodcrest Trailer Court

Rolla, MO 65401

internet: kls@umr.edu

The next version will have upgraded libraries, an editor,

and possibly, some help screens.

QUESTIONS AND/OR COMMENTS ARE WELCOME!!